APPENDIX A

Characteristics of Overhead Conductors

A.1 Characteristics of Aluminum Cable Steel Reinforced Conductors (ACSR)

A.2 Characteristics of All-Aluminum Conductors (AAC)

APPENDIX B

Matlab Circuits

B.1 Full Load Circuit

B.2 Overload Circuit

B.3 Bundle Transmission Line (Solution 1)

B.4 Parallel Transmission Line (Solution 2)

B.4 Parallel Generators and Parallel Transmission Line (Solution 3)

B.4 Distribution Generator (Solution 4)

B.4 Parallel Transformer (Solution 5)

APPENDIX C

PSS Circuit &Results

1

PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      Fri, Mar 30 2007  10:20

FULL AND OVER LOAD CIRCUIT                                               RATING

FULL LOAD                                                                 SET A

BUS     1 B1      7.50 AREA CKT    MW     MVAR     MVA  %I 1.0606PU    .00    1

GENERATION              1        39.9    20.1R   44.7  63 7.9545KV

TO     2 B2      66.0   1  1     39.9    20.1    44.7  65 1.0000RG

BUS     2 B2      66.0 AREA CKT    MW     MVAR     MVA  %I 1.0241PU  -4.38    2

1                                 67.594KV

TO     1 B1      7.50   1  1    -39.9   -16.5    43.2  65 1.0000UN

TO     3 B3      66.0   1  1     39.9    16.5    43.2  42

BUS     3 B3      66.0 AREA CKT    MW     MVAR     MVA  %I 1.0241PU  -4.38    3

1                                 67.594KV

TO     2 B2      66.0   1  1    -39.9   -16.5    43.2  42

TO     4 B4      66.0   1  1     19.5     4.4    20.0  63

TO     7 B7      66.0   1  1     19.6     6.7    20.8  66

TO     8 B8      66.0   1  1       .8     5.3     5.4  17

BUS     4 B4      66.0 AREA CKT    MW     MVAR     MVA  %I  .8864PU  -9.26    4

1                                 58.504KV

TO     3 B3      66.0   1  1    -17.2    -3.3    17.5  64

TO     5 B5      66.0   1  1      8.2    -3.9     9.0  33

TO    40 T1      11.0   1  1      9.0     7.1    11.5  86  .9000LO

BUS     5 B5      66.0 AREA CKT    MW     MVAR     MVA  %I  .8761PU -10.92    5

1                                 57.822KV

TO SHUNT                           .0   -11.5    11.5

TO     4 B4      66.0   1  1     -7.9     3.8     8.8  33

TO     6 B6      66.0   1  1     -1.6     1.1     1.9   7

TO    50 T2      11.0   1  1      9.5     6.7    11.6  88  .9000LO

BUS     6 B6      66.0 AREA CKT    MW     MVAR     MVA  %I  .8777PU  -9.62    6

1                                 57.930KV

TO SHUNT                           .0   -11.6    11.6

TO     5 B5      66.0   1  1      1.6    -1.8     2.4   9

TO     7 B7      66.0   1  1     -9.6     -.7     9.6  36

TO     9 B9      66.0   1  1     -7.0     3.1     7.7  28

TO    60 T4      11.0   1  1     15.0    11.0    18.6  85  .9000LO

BUS     7 B7      66.0 AREA CKT    MW     MVAR     MVA  %I  .9357PU  -6.68    7

1                                 61.754KV

TO     3 B3      66.0   1  1    -18.2    -6.0    19.1  66

TO     6 B6      66.0   1  1     10.2      .6    10.2  35

TO    70 T3      11.0   1  1      8.0     5.4     9.7  69  .9000LO

BUS     8 B8      66.0 AREA CKT    MW     MVAR     MVA  %I  .9883PU  -2.64    8

1                                 65.226KV

TO     3 B3      66.0   1  1      -.6    -6.2     6.2  20

TO     9 B9      66.0   1  1     13.1     3.2    13.5  44

TO    10 B10     66.0   1  1    -20.5    -3.5    20.8  68

TO    80 T5      11.0   1  1      8.0     6.5    10.3  70 1.0000RG

BUS     9 B9      66.0 AREA CKT    MW     MVAR     MVA  %I  .9062PU  -5.32    9

1                                 59.809KV

TO     6 B6      66.0   1  1      7.5    -3.5     8.3  30

TO     8 B8      66.0   1  1    -12.1    -3.1    12.5  45

TO    11 B11     66.0   1  1     -4.3     -.9     4.4  16

TO    90 T6      11.0   1  1      9.0     7.5    11.7  65  .9000LO

BUS    10 B10     66.0 AREA CKT    MW     MVAR     MVA  %I 1.0606PU   -.09   10

1                                 70.000KV

TO     8 B8      66.0   1  1     21.8     4.2    22.2  68

TO    11 B11     66.0   1  1     25.5     6.5    26.3  80

TO    12 B12     66.0   1  1     12.7     9.9    16.1  49

TO    14 B14     66.0   1  1    -60.0   -20.6    63.4  60

BUS    11 B11     66.0 AREA CKT    MW     MVAR     MVA  %I  .9279PU  -4.40   11

1                                 61.239KV

TO     9 B9      66.0   1  1      4.4      .4     4.4  16

TO    10 B10     66.0   1  1    -22.7    -4.7    23.2  81

TO    13 B13     66.0   1  1      8.3    -3.2     8.9  31

TO   110 T8      11.0   1  1     10.0     7.5    12.5  67  .9000LO

BUS    12 B12     66.0 AREA CKT    MW     MVAR     MVA  %I  .9980PU   -.32   12

1                                 65.869KV

TO    10 B10     66.0   1  1    -12.0    -9.8    15.5  50

TO   120 T7      11.0   1  1     12.0     9.8    15.5  78 1.0000RG

BUS    13 B13     66.0 AREA CKT    MW     MVAR     MVA  %I  .9105PU  -6.55   13

1                                 60.092KV

TO SHUNT                           .0    -8.3     8.3

TO    11 B11     66.0   1  1     -8.0     3.0     8.5  30

TO   130 T9      11.0   1  1      8.0     5.3     9.6  53  .9000LO

BUS    14 B14     66.0 AREA CKT    MW     MVAR     MVA  %I 1.0606PU   -.09   14

1                                 70.000KV

TO    10 B10     66.0   1  1     60.0    20.6    63.4  60

TO    15 B15     7.50   1  1    -60.0   -20.6    63.4  92 1.0000UN

BUS    15 B15     7.50 AREA CKT    MW     MVAR     MVA  %I 1.1072PU   6.01   15

GENERATION              1        60.0    28.1R   66.2  94 8.3042KV

TO    14 B14     66.0   1  1     60.0    28.1    66.2  92 1.0000RG

BUS    40 T1      11.0 AREA CKT    MW     MVAR     MVA  %I  .9521PU -11.83   40

1                                 10.473KV

TO LOAD-PQ                        9.0     6.5    11.1

TO     4 B4      66.0   1  1     -9.0    -6.5    11.1  78  .9000UN

BUS    50 T2      11.0 AREA CKT    MW     MVAR     MVA  %I  .9426PU -13.69   50

1                                 10.369KV

TO LOAD-PQ                        9.5     6.0    11.2

TO     5 B5      66.0   1  1     -9.5    -6.0    11.2  79  .9000UN

BUS    60 T4      11.0 AREA CKT    MW     MVAR     MVA  %I  .9446PU -12.23   60

1                                 10.390KV

TO LOAD-PQ                       15.0    10.0    18.0

TO     6 B6      66.0   1  1    -15.0   -10.0    18.0  76  .9000UN

BUS    70 T3      11.0 AREA CKT    MW     MVAR     MVA  %I 1.0160PU  -8.71   70

1                                 11.176KV

TO LOAD-PQ                        8.0     5.0     9.4

TO     7 B7      66.0   1  1     -8.0    -5.0     9.4  62  .9000UN

BUS    80 T5      11.0 AREA CKT    MW     MVAR     MVA  %I  .9583PU  -4.90   80

1                                 10.541KV

TO LOAD-PQ                        8.0     6.0    10.0

TO     8 B8      66.0   1  1     -8.0    -6.0    10.0  70 1.0000UN

BUS    90 T6      11.0 AREA CKT    MW     MVAR     MVA  %I  .9814PU  -7.15   90

1                                 10.796KV

TO LOAD-PQ                        9.0     7.0    11.4

TO     9 B9      66.0   1  1     -9.0    -7.0    11.4  58  .9000UN

BUS   110 T8      11.0 AREA CKT    MW     MVAR     MVA  %I 1.0060PU  -6.33  110

1                                 11.066KV

TO LOAD-PQ                       10.0     7.0    12.2

TO    11 B11     66.0   1  1    -10.0    -7.0    12.2  61  .9000UN

BUS   120 T7      11.0 AREA CKT    MW     MVAR     MVA  %I  .9644PU  -2.82  120

1                                 10.608KV

TO LOAD-PQ                       12.0     9.0    15.0

TO    12 B12     66.0   1  1    -12.0    -9.0    15.0  78 1.0000UN

BUS   130 T9      11.0 AREA CKT    MW     MVAR     MVA  %I  .9936PU  -8.14  130

1                                 10.930KV

TO LOAD-PQ                        8.0     5.0     9.4

TO    13 B13     66.0   1  1     -8.0    -5.0     9.4  47  .9000UN

--------------------------------------------------------------------------------

1     PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      Fri, Mar 30 2007  10:21

FULL AND OVER LOAD CIRCUIT

FULL LOAD

TRANSMISSION LINE LOADINGS ABOVE 100.0 % OF RATING SET A:

X-------FROM BUS-------X  X--------TO BUS--------X       CURRENT(MVA)

BUS    NAME  BSKV AREA    BUS    NAME  BSKV AREA CKT LOADING  RATING PERCENT

* NONE *

--------------------------------------------------------------------------------

1     PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      Fri, Mar 30 2007  10:21

FULL AND OVER LOAD CIRCUIT

FULL LOAD

TRANSFORMER LOADINGS ABOVE 100.0 % OF RATING SET A:

X-------FROM BUS-------X  X--------TO BUS--------X       MVA      MVA

BUS    NAME  BSKV AREA    BUS    NAME  BSKV AREA CKT LOADING  RATING PERCENT

14  B14     66.0    1     15* B15     7.50    1  1     66.2    65.0   101.9

--------------------------------------------------------------------------------

1     PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      Fri, Mar 30 2007  10:21

FULL AND OVER LOAD CIRCUIT

FULL LOAD

BUSES WITH VOLTAGE GREATER THAN 1.0500:

X------ BUS -----X AREA V(PU)  V(KV)    X------ BUS -----X AREA V(PU)  V(KV)

1 B1      7.50   1 1.0606  7.955       10 B10     66.0   1 1.0606 70.000

14 B14     66.0   1 1.0606 70.000       15 B15     7.50   1 1.1072  8.304

BUSES WITH VOLTAGE LESS THAN  .9500:

X------ BUS -----X AREA V(PU)  V(KV)    X------ BUS -----X AREA V(PU)  V(KV)

4 B4      66.0   1  .8864 58.504        5 B5      66.0   1  .8761 57.822

6 B6      66.0   1  .8777 57.930        7 B7      66.0   1  .9357 61.754

9 B9      66.0   1  .9062 59.809       11 B11     66.0   1  .9279 61.239

13 B13     66.0   1  .9105 60.092       50 T2      11.0   1  .9426 10.369

60 T4      11.0   1  .9446 10.390

--------------------------------------------------------------------------------

1     PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      Fri, Mar 30 2007  10:21

FULL AND OVER LOAD CIRCUIT

FULL LOAD

***********************  SUMMARY FOR COMPLETE SYSTEM  ***********************

SYSTEM SWING BUS SUMMARY

BUS X---NAME---X X--- AREA ---X X--- ZONE ---X       MW       MVAR   MVABASE

1 B1      7.50   1 [        ]   1 [        ]      39.9      20.1      70.6

24 BUSES          2 PLANTS             2 MACHINES       9 LOADS

26 BRANCHES      11 TRANSFORMERS       0 DC LINES

X------ ACTUAL ------X X----- NOMINAL ------X

MW        MVAR         MW        MVAR

FROM GENERATION               99.9       48.2        99.9       48.2

TO CONSTANT POWER LOAD        88.5       61.5        88.5       61.5

TO CONSTANT CURRENT             .0         .0          .0         .0

TO CONSTANT ADMITTANCE          .0         .0          .0         .0

TO BUS SHUNT                    .0      -31.4          .0      -40.0

TO LINE SHUNT                   .0         .0          .0         .0

FROM LINE CHARGING              .0        8.9          .0        9.9

VOLTAGE       X----- LOSSES -----X   X-- LINE SHUNTS --X   CHARGING

LEVEL BRANCHES      MW        MVAR        MW        MVAR       MVAR

66.0     17      11.42      21.60         .0         .0        8.9

11.0      9        .00       5.38         .0         .0         .0